Xuchang Chang an Technology Co., Ltd     CAKJ-XHB-8X~48X Microcomputer Central Signal Alarm Device                v1.1

             CAKJ-XHB-8X~48X Microcomputer Central Signal Alarm Device
1，OVERVIEW

CAKJ-XHB separate micro computer central signal alarm device is a centralized management device that designed for Power station and Transformer substation signal system. The device that extensively used in electric, petrochemical, chemical industry, metallurgy and coal industry, is a high intelligent product that automatic monitoring and signal alarm for power and industrial.

2，FUNCTIONAL CHARACTERISTICS

1）The panel includes digital display and power on self test (POST).Integrated design. 

2）Provide with test (light test), confirm (accept), return（reset）, signal recall and clear function. With function buttons.

3）Provide with manual and automatic accept function, automatic accept time limit (0-200s) able to set. 

4）Signal alarm type able to distinguish: accident signal S, warning signal Y, position signal P, all available to set. 

5）Alarm window color: able to choose red, white, yellow, green, accord to signal alarm type, separated by color is more obvious and visually.

6）Input signal status: switch contact (h), switch hold contact (E), and pulse hold contact (C). (Note)

7）The input signal is normally open and normally closed. For each signal, the normally open and normally closed alarm (default) can be set, and the normally closed variable normally open alarm can be set.
8）Signal delayed alarm: 0-9999ms delay alarm time limit able to set. 

9）Device bring with buzzer, when accident happy it sounds “bi---”, warning signal sounds short beep “bi, bi, bi, bi”, position signal doesn’t sound.

10）Device with accident and warning signal alarm output contact, able to activate electric bell, enhance the alarm effect.

11）With remote signal output contacts, connect to other devices or as an accident stop signal.

12）It has the device power disappearance contact output.

13）Provide with digital communication output, RS485 serial communication contact, MODBUS communication protocol.


◆Note: Explanation of input signal status and alarm procedures

When“h” is selected as the input signal state (default), the workflow is as follows:            

	Line
	Run
	Button
	Alarm status
	Light plate
	Sound status
	Remark

	1
	Normal
	 -
	Normal
	Off
	Silent
	

	2A
	Abnormal
	 -
	Alarm 
	Flash
	Sound
	Alarm

	2B
	Abnormal
	Silence
	Alarm 
	Flash
	Silent
	Alarm hold

	3A
	Abnormal
	Confirm 
	Comfirmed
	Bright
	Silent
	Alarm hold

	3B
	Normal
	
	 -
	To line 4
	Instant alarm

	4
	Normal
	-
	Normal
	Off
	Silent
	Automatic reset


When the state of the input signal is "C" or "E", the work flow is as follows:

	Line
	Run
	Button
	Alarm status
	Light plate
	Sound status
	Remark

	1
	Normal
	 -
	Normal
	Off
	Silent
	

	2A
	Abnormal
	 -
	Alarm 
	Flash
	Sound
	Alarm

	2B
	Abnormal
	Silence
	Alarm 
	Flash
	Silent
	Alarm hold

	3A
	Abnormal/Normal
	Confirm 
	Comfirmed
	Bright
	Silent
	Alarm hold

	3B
	Normal to abnormal
	-
	Alarm
	To line 2A
	Restart alarm

	4A
	Abnormal
	 Reset
	 -
	To line 3A
	Alarm hold

	4B
	Normal
	
	Normal
	Off
	Silent
	Manual reset


Note: The signal is normal if the signal is not alarmed, and the signal abnormal is if it is alarmed


3，CONMENT TECHNIQUE REQUIREMENT

1.Working power supply: AC or DC 80-265V wide voltage, DC24V Optional
2.Signal capacity: 8、12、16、24、32、48 Circuits

3.Input signal method: Normally open active dry contact, or active contact.

4.Alarm window: Flash window measures are 53×28 or 30×30, colors: red, green, yellow, white to choose. 

5.Alarm output: Alarm window flash, buzzer or sound equipment sounds.

6.Alarm sound: Buzzer beeps 60DB; we provide intensive sound equipment CAKJ-DL electric bell, CAKJ-DD electric whistle，Or CA-XXS-YX2  Electronic audio.

7.Contact output: 5 relay contact outputs, corresponding to power disappearance, warning alarm, accident alarm, pre-emptive remote communication (follow-up), accident remote communication (follow-up).

8.Contact capacity: AC250V, 3A pure resistance load, DC220V, 0.125A inductive load.

9.Function setup: touch button setting, 5 digits display.

10.Power consume: The whole device consumed no greater than 30W.

11.Communication contact: Standard RS485 serial communication contact, MODBUS communication protocol.

12.Insulation resistance: no less than 100 MΩ in-between input-output-power supply-cage.

13.Power frequency voltage: in-between input- output-power supply-cage, able to bear the tests of 2kV, 1min, 5mA, 50/60HZ, no signs of flashover and breakdown.

14.Capacity of resisting disturbance: able to bear 1 MHz and 100 kHz high frequency interference of attenuated shock wave. First half wave voltage amplitude common mode is 2.5 kV, different mode voltage is 1.0 kV, the product shouldn’t appear unwanted operation or failure of operate.

15.Environment condition: surrounding temperature -10℃~60℃; surrounding humidity no greater than 90%.

16.Weight: 2.5 kg.
4，DEVICE SETUP

Press “SET” set button, press “←” to move, “↑” to add 1, insert PIN (8080) into setup mode. Recording to menu indication press “SET” to turn pages for function setting. (Edition no. v1.1)

	Symbol 
	Setting content
	Operate
	Setting 
	Instruction

	C  0
	Insert PIN
	“←”“↑”
	PIN
	8080

	n. n
	total loops no.
	“SET”
	24
	n  this is factory setting

	[image: image1.png]


    30
	Setting auto 

confirm time
	“←”“↑”
	0~200s
	30s ( “0” not confirm automatically)

	d.  20
	Setting signal delay alarm time
	“←”“↑”
	0-9999ms
	20，20ms，

	y--A
	Alarm audio 

setting
	“↑”selected
	A，F，d，n
	A(A audio all on, F buzzer only, d external audio only,  n audio all off) 

	S.  1
	comm. adds.
	“←”“↑”
	0~255
	1(communication add. is the only one)

	b.9600
	Communication Baud rate
	“↑”selected
	9600/4800
	9600

	J.   0
	Memory signal  clear
	“←”“↑”
	Clear PIN
	1001(correct pin clear record)

	L01-y
	Setting 01 type
	“↑”selected，

“←”turn pages，setting signal type 

one by one
	y，S，P
	y(the device default all signals are “y” warning signals, recording every single signal type, press “↑” to choose “S” failure signal, press “↑”to choose “P” location signal, while finish, press “←” to turn pages, setting signal types one by one.

	L02-y
	Setting 02  type
	
	
	

	- - - -
	 - - - - - -
	
	
	

	Ln-y
	Setting  n  type
	
	
	

	E01-h
	Setting 01 status
	“↑”selected，

“←”turn pages，setting signal input type one by one
	h, C,E
	h（h device default switch contact）, press “↑”to choose “C” pulse type retaining contact, press“↑” to choose “E” switch retaining contact, while finish, press “←” to turn pages，setting signal type one by one)

	E02-h
	Setting 02 status
	
	
	

	- - - -
	 - - - - - -
	
	
	

	En-h
	Setting n status
	
	
	

	F01-o
	Setting 01 op/co
	“↑”selected，

“←”turn pages，setting signal open/closed one by on
	o , c
	o (Device by default, Normally open contacts closed alarm），press the "↑" choose "c" Normally closed contacts open alarm. press← to flip pages, set normally open/closed alarm them one by one.

	F02-o
	Setting 02 op/co
	
	
	

	- - - -
	 - - - - - -
	
	
	

	Fn-o
	Setting n  op/co
	
	
	

	while setting finish or no setting press “SET” button to save and exit, restore to normal alarm condition.


◆Signal unified setting table; press "SET" to enter the setting, press "←" to shift, press "↑" to add 1, after entering the code, press "SET" to complete the setting and return

	Enter code
	Set 1-n signal alarm type
	Enter code
	Set 1-n signal input status

	C1101
	Unified settings for accident signals S
	C1104
	Uniformly set as switch contacts  h

	C1102
	Uniformly set as a warning signal  y
	C1105
	Uniformly set as pulse contacts   C

	C1103
	Uniformly set as position signal  P
	C1106
	Uniformly set to keep contacts   E


Note: This setting is convenient for the user to set all signals to one type or state on site, do not operate easily.
★Light word plate alarm name printing transparent paper 

[image: image2.png]Transparent cover
= = Astigmatism

t Typing paper 1 board

v
t Astigmatism board t Typing paper
I

[ I
= |

Transparent cover

Symmetrical operation
-~ —

[ ] il THl
o - = =

\ Case | Transparent cover, print

transparent paper, astigmatism

Light plate assembly diagram| |board, installation diagram




or light board replacement diagram ☞
[image: image3.jpg]" BUSCOUPLER. PROT \\

e ‘\L
P8




53x28
[image: image4.jpg]



[image: image5.png]



Method of opening the transparent cover
[image: image6.png]| Clear

I Cover

Suit
Tiles





[image: image7.png]


[image: image8.png]


[image: image9.jpg]


30x30
5，DEVICE ALARM AND TESTING
1）POST (power on self test), when device power on, digital display window on device panel shows in sequence 【0.0.0.0.0】【1.1.1.1.1】…【7.7.7.7.7】【8.8.8.8.8】alarm window all light 【9.9.9.9.9】alarm window all light scroll display 【C- n L】(for power indicate). POST finish.  "n" is the total number of circuits of the alarm device.

2）Press  “test” button, all alarm window flash, buzzer sounds, output audio equipment act. Release test button, return to monitoring status.

3）When signal alarm, recording alarm window flash, and buzzer sounds, output audio equipment act to start electric whistle sound. Digital display window shows recording loop number.

4）Press “accept” button (or 0-200s affirm automatically), alarm window turns from flash to light, buzzer silence, output audio contact return, electrical whiles and bell silence.

5）When signal return, switch type contact input signal recording alarm window lights off. Retention type contact input signal alarm window remain alarm, require manual reset (press  “reset” button), and alarm window lights off.

6）Long press “recall” button, alarmed signals will shine one by one which followed alarm sequence by FILO (first in last out) rules. At the same time LED display shows alarmed loop, maximum 200 signals can be recalled, and alarm signals have priority.

6，Model specifications

	Model
	Alarm loop
	Series code
	signal type
	Detailed description

	CAKJ-XHB
	
	
	
	Changan integrated signal alarm device

	
	-8
	
	
	8 Loop alarm signals (8 alarm light plates)

	
	-12
	
	
	12 Loop alarm signals (12alarm light plates)

	
	-16
	
	
	16 Loop alarm signals (16 alarm light plates)

	
	-24
	
	
	24 Loop alarm signals (24 alarm light plates)

	
	-32
	
	
	32 Loop alarm signals (32alarm light plates)

	
	-48
	
	
	48 Loop alarm signals (64 alarm light plates)）

	
	
	X
	
	X series size, Standard type

	
	
	X2 or X3
	
	X series non-standard improved type (size change)

	
	
	
	blank
	Alarm signal is passive dry contact signal input

	
	
	
	-A
	Alarm signal is active voltage signal input
(DC220V, DC110V, etc., specified when ordering)


Example：CAKJ-XHB-32X  Central signal alarm device (32 Loop passive signal input alarm)
    CAKJ-XHB-32X-A  Central signal alarm device (32-Loop active signal input alarm, DC220V)
System wiring diagram 

◆ Basic control operation circuit
[image: image10.png]KM+ - [+ o
K s K [bowerbus
701
o Al A2 1020 o | X2 702, Power
CA-XNS-TX
. fEm CAKJ-DD supply
- 1 2l ¢ - Dj Accident
B5 B6 alarm,
B5 B6| |4 . G ®—e electric
s [/ CAKJ-DL whistle
B3 B4 " B3 " Q 'Waming
, . @ [alam bell
Electronic Electric B
B2 ower
P —BE i El B2 e disappear
B8 B7 B7| whistle Warnin;
P B8 |distant signal
BA B9 BA - B9 Accident
distant signal
X1 —RS4854 X1—RS4854 Commun-
X2|— RS4858 X2|— RS485B ication






[image: image11.png]8.12.16.24 button and external button function 32,48 button and external button function

Devi Nl [Test NI Test
—1 e 1 -
?t‘]’llce —N2—  —|If you |Accept —N2 Ifyou |Accept
wi == N3 Ineed [Reset Device N3 —— need |Silence
button - N4l |eanbe with | 1 |canbe [Reset
Recall —N4
outer button | L |outer el
Except join —No join cca
12X2 N6 Unattended
G com2 4 com2





◆ Signal input circuit wiring diagram
[image: image12.png]CAKJ-XHB—nX

Passive signal input circuit

01

02

cooooo

03

cooooo

External
contacts

1GP
2GP
3GP

cooooo

n-1GP
nGP

Passive
signal
(signal
voltage
DC24V
provided
inside the
device)
Input

COM1

CAKJ-XHB-nX-A

Signal power|

Active
signal
(externally
supplied
signal
voltage
DC220V.
DC110V.
etc.)
Input

COM1

XM+ C O ;! .. XM=
- Active signal input circuit ——
[ 2 01 1GP
® 02 2GP
* 03 3GP
o o o
. . .
o o .
o o o
o o o
® 15— [n-16P
[ 2 n nGP
External % ?
contacts





◆ Schematic diagram of passive dry contact and active voltage signal input
[image: image13.png]External

V External contacts

Signal 1 (GP1)
CPU
Device
24V-

Signal com. 24V+

Passive (no voltage) signal input

|~ External contacts

“—— G0 Sigmal 1 (GPD)

CPU__
voltage EXxternal Device
- ——————| 3 Signal com. DC-

Active (with voltage) signal input





8，Detailed description of signal device

◆8-circuit central signal alarm device

1. Model and specifications

	Product Model
	Alarm Circuit
	Input Signal Type
	Signal Voltage
	Power supply 

	CAKJ-XHB-8X
	8 Circuits
	Passive dry contact signal input
	not have
	AC or DC
80-265V

	CAKJ-XHB-8X-A
	8 Circuits
	Active voltage signal input
	DC110V,DC220V etc
	


[image: image14.jpg]c5

04 05 06 0( 09 10 11 12

01 02 03
A A

{5 2% A signal input m
B2 B3 B4 EB5

Al AZ A3 El B6 BT E3 B9 BA C4 N1 N2 N3 N4 X1 X2 GND
e LT i AT A

N
Power Switch

"AKJ-XHB 8X

4 5 MODEL : (
ZHAENAME : 1) 2 17,
AL S INPUT SIGNAL: | %< Dry
JREE[O] 55 ALARM CHANNF HANNI

L {1 i WORKING POWER - AC/D v
B EI DATE OF PRODUCTION
48 'S NUMBER: 16042101

TR
XuChang changAn tec

& 3R RN CRT
BEMAE (T, T
All of the input
signal contact.
supply, while the signal
you won't call the police,

risk of burning equipwment

is no pow
don

External

and

VLT R





[image: image15.jpg]


2. 8X appearance graphics
3. 8X appearance and installation hole size
[image: image16.png]160

©  Microcompute conal sigl sl dvics CAKLEB-S
1GP 2GP 3GP 4GP
5GP 6GP TGP 8GP
C-08L |® ©@ © wn O O O O

297

150

152

Hole Size

95

289






4. 8X wiring and location diagram
[image: image17.png]01 02 03 04 05 06 07 08 09 10 11 12 C5

0‘10‘20‘30‘40‘50‘60‘70‘809101112C5
i l External
\\\\\\\\T\\\\\\ contact
1-8 Signal input lcoM1
AlAZAf BlBZBSMBSBGB7BBBQBAC4N1N2N3N4X1X2GND
‘ ‘j L. J J L ‘ ‘
© = =) =)
e |E o = I I B - =
212 |8 2ol8 g =1 = A A
= I <o |- < 5 e}
glzle| |2 |EE[3E (2858 0|88 85|38 |2
o | SolSo|d5|2 32 B2 &2 8|8 |8
8 |= a|l= a|= 5|< 0
Power FULL Audio output [Remote signall External  |Cammication|
Supply contacts output button [interface

Al A2 A3 B1 B2 B3 B4 B5 B6 B7 B8 B9 BA C4 N1 N2 N3 N4 X1 X2 GND





Note: External buttons: common, test, confirm, reset, recall, and audio output terminals. Multiple sets of devices can be connected in parallel, sharing one set of buttons and audio. The corresponding terminal block can be installed in any combination. Note that the buttons or switches connected in parallel must be passive dry contacts.

◆12-circuit central signal alarm device

1. Model and specifications

	Product Model
	Alarm Circuit
	Input Signal Type
	Signal Voltage
	Power supply 

	CAKJ-XHB-12X
	12 Circuits
	Passive dry contact signal input
	not have
	AC or DC
80-265V

	CAKJ-XHB-12X-A
	12 Circuits
	Active voltage signal input
	DC110V,DC220V etc
	


2. 12X appearance graphics

[image: image18.jpg]


[image: image19.jpg]



3. 12X appearance and installation hole size
[image: image20.png]205

© Microcomputr cental sigaal alarm devios CAKIXHBIX

1GP 2GP 3GP 4GP

5GP 6GP TGP 8GP LO D~
> for Hole Size
| H i

9GP 10GP 11GP 12GP

Tijecom O OO O

svur  RESED s
)]

289

297 .90 |





4. 12X wiring and location diagram
[image: image21.png]ANDSG8YSY

4-G87Sy

Y-G87SY

[Camnication)

ARCEEN

1959y

1do00y

44 ‘ ‘ 1L

1s3]

button

2IW0d

andino
JUap 1Oy

3ndino
Sutuxey

External
contact

punos
Juep IOy

‘COMI ‘

punos;
Sutuxey

Audio output |Remote signall External
output

contacts

o
B
-
1
=
B3
©
2
I
P
=
=
By
o
-
e
=
=}
2}
=}
=
m
©
=)
=)
)
)
@
o1
=}
—
/m

Bl B2 B3 B4 B5 B6 B7 B8 B9 BA C4 N1 N2 N3 N4 X1 X2 GND

ULL

aanyrey oq|

F

ad

-oa

Power
Supply

Al A2 A3

+2a

1-12 Signal input

01 02 03 04 05 06 07 08 09 10 11 12 C5
01 02 03 04 05 06 07 08 09 10 11 12 C5





◆16-circuit central signal alarm device

1. Model and specifications

	Product Model
	Alarm Circuit
	Input Signal Type
	Signal Voltage
	Power supply 

	CAKJ-XHB-16X
	16 Circuits
	Passive dry contact signal input
	not have
	AC or DC
80-265V

	CAKJ-XHB-16X-A
	16 Circuits
	Active voltage signal input
	DC110V,DC220V etc
	


2. 16X appearance graphics
[image: image22.jpg]


[image: image23.jpg]10KV k',l]f‘ﬁ
L il 1 i b 5%

10kV) AR
s [ T





3. 16X appearance and installation hole size
[image: image24.png]205

[ ————— EvTE——
1GP 2GP 3GP 4GP
5GP 6GP TGP 8GP
s N Hole Size
9GP 10GP 11GP 12GP = |:| =
13GP 14GP 15GP 16GP
cijecom OO OO
Y e w S

297 90 289





4. 16X wiring and location diagram
[image: image25.png]13 14 15 16

01 02 03 04 05 06 07 08 09 10 11 12 C5

13 14 15 16

01 02 03 04 05 06 07 08 09 10 11 12 C5

External
contact

1)

aNOS87SY

4-G87Sy

Y-G8%SY

|Camuni cation|

T1B99Y

EEEER

13-16 Signal input

444 ‘ ‘ 1

ICOM1

1-12 Signal input

B1 B2 B3 B4 B5 B6 B7 B8 B9 BA C4 N1 N2 N3 N4 X1 X2 GND

LJ L)L) L L

3daooy

1sa]

ZWod

button

3ndino
JUaPTO0Y

3ndino
Sutuxey

punos
JUepTOdy

punos
Sutuiey

Audio output |Remote signal| External
output

contacts

san[iey 00

FULL

dd

-oa

+2a

Power

Supply

o
B
-
1
=
B3
©
2
)
=
=
=
By
o
-
e
=
=}
2}
=}
=
m
©
=)
=)
)
)
@
o1
=}
—
/m

Al A2 A3





◆24-circuit central signal alarm device

1. Model and specifications

	Product Model
	Alarm Circuit
	Input Signal Type
	Signal Voltage
	Power supply 

	CAKJ-XHB-24X
	24 Circuits
	Passive dry contact signal input
	not have
	AC or DC
80-265V

	CAKJ-XHB-24X2
	24 Circuits
	Passive dry contact signal input
	not have
	

	CAKJ-XHB-24X3
	24 Circuits
	Passive dry contact signal input
	not have
	

	CAKJ-XHB-24X-A
	24 Circuits
	Active voltage signal input
	DC110V,DC220V etc
	

	CAKJ-XHB-24X2-A
	24 Circuits
	Active voltage signal input
	DC110V,DC220V etc
	

	CAKJ-XHB-24X3-A
	24 Circuits
	Active voltage signal input
	DC110V,DC220V etc
	


2. 24X appearance and installation hole size
[image: image26.jpg]


[image: image27.png]197

Installation
hole size

374




[image: image28.png]205

© Mictocemputercenal sgeal alamm device

CAKJ-XHB-24X

1GP 2GP 3GP 4GP 5GP 6GP
TGP 8GP 9GP 10GP 11GP 12GP
13GP 14GP 15GP 16GP 17GP 18GP
19GP 20GP 21GP 22GP 23GP 24GP
Tle o0 KR X

RECALL

FESET ACCEPT

TEST

382





[image: image29.png]263

1GP 2GP 3GP 4GP
5GP 6GP TGP 8GP
=
9GP 10GP 11GP 12GP Mounting
brackets
13GP 14GP 15GP 16GP
17GP 18GP 19GP 20GP
21GP 22GP 23GP 24GP
sG] 2 0.0 ) (@1 0 OO0

ST ——

Rasmt
El

Acer
ES

263




3. 24X2 appearance and installation hole size
[image: image30.png]255

FILRS
Hole size




[image: image31.jpg]01 02 03 04 05 06 07 08 09 10 11 12 C5

.01 02 03 04 05 06 07 08 09 10 11 12 C5 13 14 15 16 17 18 19 20 21 22 23 24 G5
kkkkakLLkLL|LLl I lL’
‘ signal input |COI]l L_ signal input IOMI]

A2 A3 El B2 B3 B4 B5 B6 B7 B8 E9 BA C4 N1 N2 N3 N4 X1 X2 GND
P N O I P T

omosoassy | —2

£ | pe Failure

1
|
| A1 A2 A3

B1 B2 B3 B4 B5S B6 B7 B8 B9 BA C4 N1 N2 N3 N4 X1 X2 GND




[image: image32.jpg]TR MAX. MAIN i "
OIL LEVEL ALARM I

OLTG PRESSURE
RELIEF DEVICE
RIP

I'l AC POWER
FAILURE

0LTC MOTOR
BREAKER TRIP
| |
TAP CHANGE  [ij i SPARE i
INCOMPLETET " ;
| :

‘0000
e BUZZER RE 2





4. 24X3 appearance and installation hole size
[image: image33.png]152

Hole Size

289




[image: image34.png]160

G- Microcomputer cerra sigrat sarm device

T

ep || 2 || sop || 4op|l sop || ecp || 7ep || sce

9cp || 100 || 11cp |l 126p || 130 |l 14cp [f15cp | 1608

w7cp || 18cp || 190 || 20p || 210p |l 220 [loace |l 240p

ch24L| B ® @ po @ O @ Q
B

il

297




[image: image35.jpg]514 15 16 17 18 192021 2223 21 G5
(TG ICET

L

8 8% Asignal input z20ve [t |

CAKIIQK!MXIXZGHB

BA
gl




[image: image36.jpg](= Microcomputer central signal alarm device

e Il e

R H R

RS | SVLEREE

| S
| o

(=8
a5

PR Bk

f=a
| =]

EEm- oo -

BUZZER
N 2%

WEL B
\

1*-%: kil
(R4 Bk ]

f5%

& g

ERAP Bk el
(*_‘ 1

e ]

LB
At {8

]
20H5 1 AR |
| fRe Bk

=

{=E





5.  Wiring and location diagram
[image: image37.png]01 02 03 04 05 06 07 08 09 10 11 12 C5

[
13 14 15 16 17 18 19 20 21 22 24 24 (5

01 qZ q3 0‘4 q5 qﬁ q7 qS q9 1‘0 1‘1 1‘2 C5
|

13 14 15 16 17 18 19 20 21 22 23 24 C5
P — 1

External

\\l \\\\\i\iiiiil

\J

contact |

Signal input

coML Signal input cout

Al A2 A3

B1 B2 B3 B4 B5 B6 B7 B8 B9 BA C4 N1 N2 N3 N4 X1 X2 GND

UL L L L 4L

5k 2l s | 5|3 |2 oo lalTlE |B

| o S| . < Bel o alel—|w(w B
ala = 0F = S S lalelelew B0 | @
glolel [<Z 25|22 Bl2I8l2l8|2|2|2
2| am| 4 2 I = [Sle|<=|x|ex || | &
Power Fault| Audio output [Remote signal| External |Cammication
supply contacts loutput button interface

Al A2 A3 Bl B2 B3 B4 B5 B6 B7 B8 B9 BA C4 N1 N2 N3 N4 X1 X2 GND





◆32-circuit central signal alarm device

1. Model and specifications

	Product Model
	Alarm Circuit
	Input Signal Type
	Signal Voltage
	Power supply 

	CAKJ-XHB-32X
	3 Circuits
	Passive dry contact signal input
	not have
	AC or DC
80-265V

	CAKJ-XHB-32X2
	32 Circuits
	Passive dry contact signal input
	not have
	

	CAKJ-XHB-32X-A
	32 Circuits
	Active voltage signal input
	DC110V,DC220V etc
	

	CAKJ-XHB-32X2-A
	32 Circuits
	Active voltage signal input
	DC110V,DC220V etc
	


2. 32X appearance and installation hole size
[image: image38.png]219

Installation
hole size

374




[image: image39.png]5

227

CAKI-XHB=32X
1P || 26p || sep || acp || scp || ecp
76 || sep || ocp || 1oep || 11ep || 120P
136P | | 146p || 156p || 160P || 170P || 186P
1960 | | 200p || 216p || 220p || 236p || 240p
256p | | 26p || 27cp || 2scp || 20cp || 30cp
316P || 320P ool wm QOO0

382




[image: image40.jpg]s e warning

DC110V T : —_——
! BB G MR AR,
KM R LR i
| ALl of the input signal is
e ST ; | signal contact. External don’ |
Al A2 (I=ORE03 25 | supply, while the signal acce:

5]

Bl B2 B7 B8 B9 BA X1 X2 XG y [
:Vriskrof burning equipment.

AR G

A
to follow | communication Can pick up when external button (need)

& A AIE QUAL TF I
W4 MODEL : CAK J-XHB-32X ;
£ FRNANE : o S (R 5 R 8 T CONTRAL SIGNAL
il Afi 5 INPUT SIGNAL: {24 Dry conta
JRB[0] 3% ALARM CHANNEL : 82 #§ CHANNEL
[ fF (L WORKING POWER:DCLIOV P G0W
41 HIWIDATE OF PRODUCTION: 2016/08/:
¥4 NUMBER : 16030676

@, T SR 2w
XuChang changAn tecl

u

Pawer Switeh




[image: image41.jpg]| AC Power
failure

MCB Alarm

-

OLTC 01l Level Gauge
High Level Alarm

Il AC Power
failure

Signal
Motor Circuit

Main Gas Relay *

Alarm

.

‘Incomplete Switching

Control Power
failure

Operation

Group 1 Fans
failure

f‘ ank 0i| Level Gauge’
1¢ High Level Alarm

- em g

Group 2 Fans
failure





[image: image42.png]Al 42 A3 B1 B2 B3 B4 BS B6 BT B8 BY BA NC NC X1 X2 XG 01 02 03 04 05 06 07 08 09 10 11 12 13 14 15 16 C5 C5 17 18 19 20 21 22 23 24 25 26 27 28 29 30 31 32 C5 C5

AL A2 A3 BL B2 B3 B4 BS E6 B7 BS B9 BANC NC x1 %2 1 0102103 04 05 06 07 08 09 10 11 12 13 14 15 16 €5 G5 Vil munnunsnnmnnuniss
RESV AR [L o I I ISy Y9y ] RRRREEEEEEEEREENN
T - N N N N

° o - g Signal input com Signal input coml
g A =R g ¢
ERMEELE et el e b
EREL R R e
a B e e e E E R
P ] ] P e

C4 C4 NC NC NG N5 N4 N3 N2 N1

IERERRER

Silence

Recall
Reset
Accept
Test

OM2
Spare
Spare

unatt.

External buttons (if needed)

C4 C4 NC NC NG N5 N4 N3 N2 N1





3. 32X2 appearance and installation hole size
[image: image43.jpg]=

Microcomputer central signal alarm device

|
e

| IRVBEGRE. |

fﬂ) ww

EEE o -

BUZZER
400 2%

4T

| Priish 5%

B oanii g |

e
%8

s I
2AH4FR A

{R4r Bk e

J =

=T





[image: image44.png]Al A2 A3 B1 B2 B3 B4 B5 B6 BY B8 BO BA NC NC X1 X2 XD 01 02 03 04 05 06 07 08 09 10 11 12 13 14 15 16 C5 C5

Al A2 A3 B1 B2 B3 B4 B5 B6 B7 B2 B9 BA XA ¥B X1 X2 ¥D 01 02 03 04 05 06 07 08 09 10 11 12 13 14 15 16 C5 C5
PILL UL LTI S SV Y L
sEs| |2 |5.5|5.3 NN Signal input cont
S5 8|e| S (2353 AHHHEEE
g2 |¥| g |£25]835 55| 3|8(212]2
Pover Supoly | Ao outout [Repete S8 Gomication

17 18 19 20 21 22 23 24 25 26 27 28 29 30 31 32 C5 C5

ERRREERREEER RN

Lamp Test

Unattended|
Silence

Signal input ‘ comt ‘

Recal |
Reset.
Accept.

con2
Spare

External button

C4 C4 N3 N7 N6 N5 N4 N3 N2 N1 17 18 19 20 21 22 23 24 25 26 27 28 29 30 31 32 C5 C5





[image: image45.png]210

1 2 3 4 5 6 7 8
9 10 11 || 12 13 || 14 ||15 16
17 18 19 || 20 210 22 ||23 24
25 26 2711 28 29 |1 30 || 31 32
C-32jJecor O @ @ @
RECALL RESET ACCEPT Test
©

297





[image: image46.png]203

Hole Size

290





◆48-circuit central signal alarm device

1. Model and specifications

	Product Model
	Alarm Circuit
	Input Signal Type
	Signal Voltage
	Power supply 

	CAKJ-XHB-48X
	48 Circuits
	Passive dry contact signal input
	not have
	AC or DC
80-265V

	CAKJ-XHB-48X2
	48 Circuits
	Passive dry contact signal input
	not have
	

	CAKJ-XHB-48X-A
	48 Circuits
	Active voltage signal input
	DC110V,DC220V etc
	

	CAKJ-XHB-48X2-A
	48 Circuits
	Active voltage signal input
	DC110V,DC220V etc
	


2. 48X appearance and installation hole size
[image: image47.png]319

Installation
hole size

374




[image: image48.png]327

CAR] —XHB~4BK.

1GP 2GP 3GP 4GP 5GP 6GP
7GP 8GP 9GP 10GP 11GP 12GP
13GP 14GP 15GP 16GP 17GP 18GP
19GP 20GP 21GP 22GP 23GP 24GP
25GP 26GP 27GP 28GP 29GP 30GP
31GP 32GP 33GP 34GP 35GP 36GP
37GP 38GP 39GP 40GP 41GP 42GP
43GP 44GP 45GP 46GP 47GP 48GP
([CJeee] = O O O O

382




[image: image49.jpg]b i N R R .

EEERELT, SN, -

i QMEEJF«E@E‘E




[image: image50.jpg]|1 AC Power
failure

| AC Power
failure

Control Power Power

Group 1 Fans
failure ‘ full stop ‘ failure

Group 2 Fans
failure

Signal

Incomplete Switching! E| | Tank Oil Level Gauge
Motor Circuit

Operation Low Level Alarm

OLTC 0il Level Gauge Main Gas Relay |
High Level Alarm Alarm

— i

R —

B Y| ]

i ! 0il Temperature | inding Temperature

Temperature i . 1
I:’lil“to( 1; Alarm . Indicator 2# Alarm g He Indicator Alarm

——

. - A‘ : or. ree Maintanance Breathe ree Maintanance Brea ‘ i ree Maintanance Breathe
'u\'d n|d ng T:me;gtpure | . 1§ Regen Status | 2% Error Status  Ji 2% Regen Status
icator Tri | ) o





3. 48X2 appearance and installation hole size
[image: image51.png]394

T35

1GP 26P 3P || 40P 5GP
6GP P || 8P 9GP || 10GP
11GP || 126P || 13GP || 14cP || 150P
160P || 17cP || 18P || 196P || 20cP
216P || 22GP || 23GP || 24P || 25GP
26P | | 276 || 28cP || 29cp || 30GP
316P || 320P || 33cP || 34GP || 35GP
36P || 37cP || 38cP || 39cP || 40cP
416P | | 426P | | 43cP || 44cp || 456P
46GP || 47GP || 48GP O O
[Joeo o O (-)

324




[image: image52.jpg]


[image: image53.jpg]ERFR
AT
O —





[image: image54.png]386

Installation
hole size

316





4.  Wiring and location diagram
[image: image55.png]A1 A2 A3 B1 B2 B3 B4 B5 B6 E7 BB B9 BA NC NC X1 X2 X0

0L 02 03 04 05 06 07 08 09 10 11 12 13 14 15 16 C5 C5

171819 20 21 22 23 24 25 26 27 28 29 30 31 32 C5 C5

0L 02 03 04 05 06 07 08 09 10 11 12 13 14 15 16 C5 C5

171819 20 21 22 23 24 25 26 27 28 29 30 31 32 C5 C5

Al A2 A3 Bl B2 B3 B4 E5 B6 E7 EB E9 EA NC NC X1 X2 XC B RN S R TP RRETRTIYTTS
RSN AN DI T Y T I T
* - olw |2 " 2 Signal input oont Signal input oont
RPN L IIE|e
R R E I AR
2 PR E[EE |89E | 2dd| 88 A= 2 (B |2
o sty | S [ T, | e

€4 C4 C NC N6 N5 N4 N3 N2 NI

Reset
Test

unatt.

conz
Spare
Spare

External buttons (if needed)

SouseeuoEaopER RN
NEEEEEEREEREREEEE

comt Signal input

C4 C4 KC NC N6 NS5 N4 N3 N2 NI

C5 C5 48 47 46 45 44 43 42 41 40 30 38 37 36 36 34 33





 CAKJ-DL, DD Electronic bell and whistle (optional)


1、Overview

    CAKJ-DL, DD electronic bell and whistle, is a low-power, non-interference, and high-volume electronic alarm device designed for central signal alarm in the power system. Using a microcontroller to simulate the sound spectrum of an electromagnetic bell and whistle, its sound is 98% similar to that of an electromagnetic bell and whistle.

[image: image56.jpg]


[image: image57.jpg]


2、 Model specifications

CAKJ-DL Electronic Bell

CAKJ-DD Electric whistle

3、 Technical parameters

Working power supply: AC, DC80~265V, wide voltage AC/DC universal,
 DC24V specified when ordering

Power consumption: not more than 3VA

Sound volume: 120DB

Electric ringtone: beeping, continuous sound

Electric flute sound: beep, uninterrupted sound

Working mode: Power on sounds, power off sounds silent Dielectric performance

Isolation voltage: Input terminal to ground 3000V, 1min

Insulation resistance: ＞ 100M Ω.

Anti interference ability: The product can withstand the electrical fast transient pulse group immunity test with a test level of 4 specified in Chapter 5 of GB/T 17626.4-2008

Applicable environment: temperature -25~55 ℃, humidity not exceeding 90% RH

Mean time between failures: not less than 50000h

4、 External dimensions and wiring

External dimensions: 80x110x100mm

Installation method: 35mm guide rail installation
[image: image58.png]



[image: image59.png]Signal alarm device

Power
supply

CAKJ-DD
B5 B6 E%

CAKJ-DL
B3 B4 9

Electric
whistle

©®

Bell alarm





Electronic audio system (optional)

1、 Overview

CA-XXS-YX2 electronic audio system is a low-power, non-interference, and high-volume electronic alarm device designed for central signal alarms in power systems. Using a microcontroller to simulate the frequency spectrum of electronic audio systems (fire and rescue sounds), electric bells, and electric horns, its sound is 98% similar to that of fire, rescue, electromagnetic electric bells, and electric horns. It has dual speakers and dual tones, and the tone volume can be adjusted.

2、 Technical parameters

Working power supply: AC, DC80-265V, wide voltage AC/DC universal, DC24V specified when ordering

Power consumption: not exceeding 5VA

Adjustable volume: 120DB high and 60DB low can be selected by pressing the "volume" button

Tone options: Electronic audio system, electric bell and flute sound can be selected by pressing the "Tone" button

Alarm circuit: 2 signal inputs, accident audio contact and warning audio contact.
Working mode: Connect the signal to sound, disconnect the signal silently.
Sound test: Press the test button, the accident and warning will sound simultaneously, and the indicator light will light up.

Indicator lights: 6 LEDs, power, test, tone, volume, accident, and warning.

Among them, the tone LED (not on - electronic sound system, on - electric bell and whistle),

Volume LED (off bass, on treble)

Button: 3 buttons for testing, tone, and volume.
Dielectric performance

Isolation voltage: Input terminal to ground 3000V, 1 minute

Insulation resistance: ＞ 100M Ω.

Anti interference capability: The product can withstand the requirements specified in Chapter 5 of GB/T 17626.4-2008

Test level 4 electrical fast transient pulse group immunity test

Applicable environment: Temperature -25~55 ℃, humidity not exceeding 90% RH

Mean time between failures: not less than 50000h

3、 Installation and wiring

Fixed with brackets or suspended behind the disc with accessories for hole embedding

External dimensions: 210X135X92

Opening size: 202X127

[image: image60.png]POWER TEST TONE VOL. AGC. PRE
® C O O O O
R RE 58 B2 BY W&

TEST TONE VOLUME

@ OO

o =i =8

TONE
() Electronic audio

{;}Electric bell and whistle

VOLUME
O Low volume

{i}High volume




[image: image61.jpg]% @u  CA-XXS-YX ELECTRONIC AUDIO SYSTEM

‘ ACC\ DENTm /PRI! ALh
| | (@ |

(((0)» o )))

BRERE MERE

POWER TEST TONE  VOL. ACC. PRE

TONE
QO Electronic audio
{F Electric bell and whistle

o o ® o 9 @
R Wk aa SE TN OME

TEST T(?NE VOLUME T
( \ ( N\ O Low volume
: LF High volume
=

W =i =55 2




[image: image62.jpg]© @ CA-XXS-YX ELECTRONIC AUDIO SYSTEM 8

ACCIDENT ALARM PRE ALARM

() | (@),

EHHE s R

POWER TEST TONE  VOL. ACC. PRE
TONE

QO Electronic audio

@ =) ® o L) ®
BB Wi SR SE TN M
{"} Electric bell and whistle

HEST T(_)NE VOI:UME L
( \ ( \ O Low volume
; ¥ High volume

W =i =5 @





[image: image63.png]KM7 5
; CA-XXS-YX2 B
R e
1 2
Signal alarm device supply
B6 JD L
= ‘ 4 Electric
—/ whistle
5 alarm
B~ m 6 {% M
7 Bell alarm





TEL：0374-3321607      http://www.xjca.com


