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                        JQA100 Series Under-Current Relay
◆ Functions
The JQA100 adjustable under-current relay is applicable to 10kV high-voltage or 400V low-voltage circuits and electrical equipment for single-phase current detection and control. It features an adjustable measuring range of 0~10A, high adjustment and detection accuracy, and fast operating speed, serving as a simple and reliable under-current relay protection device for high and low voltage systems.
◆ Technical Specifications
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Rated Current: AC5A, AC10A or 0.5A (customizable upon customer request) Under-Current Adjustment Range: 0-0.5A, 0-5A or 0-10A (currents above 10A shall be connected via current transformers) Adjustment Step: Stepless continuous adjustment Protection Logic: The relay operates when the measured current drops below the set value; the relay resets when the measured current rises to 1.2 times the set value. Control Accuracy: 2%Ie Reset Coefficient: ≥1.2 Operating Time: ≤100ms Operating Power Supply: AC220V±10% or DC24V; DC220V (80~265V) to be specified when placing orders.
Output: 1 changeover contact or separate

 1 normally-open & 1 normally-closed contact 

Rated Resistive Load Capacity: AC220V, 3A 

Overall Dimension: 48×48×90mm 

Mounting Type: DIN rail base mounting or panel flush mounting

◆ Main Product Model Specifications
	Model
	Auxiliary Power Supply
	Output Type
	Mounting Method

	JQA101
	AC220V
	1 changeover contact
	DIN rail base type

	JQA101C
	AC220V
	Separate 1NO & 1NC contacts
	DIN rail base type

	JQA102
	AC220V
	1 changeover contact
	Flush panel type

	JQA102C
	AC220V
	Separate 1NO & 1NC contacts
	Flush panel type

	JLA103
	DC24V
	1 changeover contact
	DIN rail base type

	JLA104
	DC24V
	1 changeover contact
	Flush panel type


Ordering Model Examples:
JQA101/5A Under-Current Relay (Rated 5A) JQA101/10A Under-Current Relay (Rated 10A)
◆ Terminal Wiring Diagram
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◆ Mounting Instructions
DIN Rail Base Mounting: Fix the 8-pin relay socket onto a standard 35mm DIN rail, or fasten it directly to the mounting plate via screw holes.
Flush Panel Mounting: Cut a 45×45mm square opening on the installation panel, then secure the relay to the panel with mounting brackets.
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