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WK-M（TH）Series dew controller

●功能Function 
一路凝露监控。湿度过大或将有凝露产生时，自动启动负载，调节湿度至预设值。Single way dew controller. When humidity become greater or dew may occur, the load will start automatically, adjust humidity to preset value.
●技术特性Technical characteristics
凝露启控dew control start range：88%RH±5%（20℃）

响应速度Response speed：典型值typical≤5s

负载控制Load Control：自动Automatic
工作电压Operating voltage：AC220V±10%（特殊规格订货指明particular specifications must specified in contract），AC127V

输出Output：1倍工作电压1 times voltage额定功率阻性负载Rated power resistive load: AC220V，3A

尺寸 Dimension：48×48×78mm²
●产品型号Product model
	型号
	控制方式Control
	安装方式Installation

	WK-M1（TH）
	自动Automatic
	基座式Pedestal

	WK-M2（TH）
	手动/自动Manual / Auto
	基座式Pedestal

	WK-M1Q（TH）
	自动Automatic
	嵌入式Embedded

	WK-M2Q（TH）
	手动/自动Manual / Auto
	嵌入式Embedded


●操作Operation：
WK-M1凝露控制器自动监测环境湿度，当环境湿度达到预定值88%RH时，控制器自动启动负载，当环境湿度达到预定值75%RH时返回。WK-M1 dew controller will automatically monitoring ambient humidity. When the humidity reach preset value 88% RH, the controller will start load automatically, when humidity reach preset value 75% RH controller will return to normal state.
WK-M2凝露控制器面板设有手动/自动控制开关：①将开关拨至自动位置，控制器自动监测环境湿度，当环境湿度达到预定值88%RH时，控制器自动启动负载，当环境湿度达到预定值75%RH时返回。②在正常环境条件下（环境湿度≤88%），将开关拨至手动控制位置，控制器立即启动负载开始工作，将开关拨至自动控制位置控制器返回。
WK-M2 dew control panel has manual/ automatic control switch: ① switch to automatic position, controller will monitoring humidity automatically, when the humidity reaches a preset value 88% RH, controller will start load automatically, when ambient humidity achieve preset value 75% RH controller will return to normal state. ② Under general environmental conditions (ambient humidity ≤ 88%), switch to manual control position, controller will start load, then switch to automatic control position the controller will return to normal state.
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●安装方式Installation
1.基座式：将8芯继电器座固定在35mm导轨或通过安装螺孔直接固定在安装板上。
Pedestal: Fixe 8-pin Relay Socket on 35mm rail or installing directly the mounting plate through assemble screws.
  2.嵌入式：在安装面板上开具45×45mm²孔，通过安装支架将温控器固定在面板上。
Embedded: Trepanning 45 × 45mm² hole on mounting plate, then fix controller on plate through mounting bracket.
DRC型加热板（可选件）DRC-model heating plate (optional)
1.DRC系列加热板与WK系列温湿度控制器配套使用，主要应用于电力系统高低压开关柜、箱式变电站等电器设备需要环境温度、湿度调节及凝露控制的场合。

DRC series heating plate use together with WK series temperature and humidity controller, mainly used on electric systems high and low voltage switch cabinet, box-type substation and other electrical equipment which require ambient temperature, humidity and dew control adjustment.

2.主要技术参数  电源：AC220V,50HZ(特殊电压用户注明)，AC127V。
 Main technical parameters: Power supply: AC220V, 50HZ (particular voltage specified in contract), AC127V.
有效寿命：17280小时actual service life: 17,280 hours
表面温度：100℃-120℃Surface temperature: 100 ℃ -120 ℃
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耐压：2KV,1min withstand voltage: 2KV, 1min
3.规格及型号Specifications and models                                              

	名称Name
	型号Model
	功率Power
	外形尺寸Dimensions L×W×H

	加热器

heater
	DRC-100W-AC220V
	100W
	135×85×25

	
	DRC-150W-AC220V
	100-150W
	150×100×25

	
	DRC-200W-AC220V
	150-200W
	150×100×25
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